## Principal
|  | www.valsteam.com |  | adca@valsteam.com
PHYSICAL PROPERTIES OF SATURATED STEAM
| Gauge Pressure |  | 17 | barg
| Absolute Pressure |  | 2.413 | bar
| Temperature |  | 126.3 | °C
| Specific Volume |  | 0.743 | m3/Kg
| Specific Enthalpy of Liquid |  | 126.8 | Kcal/Kg | 530.8862 | KJ/Kg
| Specific Enthalpy of Vaporization |  | 522.2 | Kcal/Kg | 2186.347 | KJ/Kg
| Specific Enthalpy of Saturated Steam |  | 649 | Kcal/Kg | 2717.2332 | KJ/Kg
SFW.ST Rev. 00

## Tabela Vapor Saturado (hidden)
Gauge Pressure - Pm (bar) | Absolute Pressure - Pa (bar) | Temperature - T (°C) | Specific Volume - V (m3/Kg) | Specific Enthalpy of Liquid - he (Kcal/Kg) | Specific Enthalpy of Liquid - he (KJ/Kg) | Specific Enthalpy of Vaporization - r (Kcal/Kg) | Specific Enthalpy of Vaporization - r (KJ/Kg) | Specific Enthalpy of Saturated Steam - hg (Kcal/Kg) | Specific Enthalpy of Saturated Steam - hg (KJ/Kg)
0 | 1.013 | 100 | 1.673 | 100.1 | 419.0987 | 539.4 | 2258.3599 | 639.5 | 2677.4586
0.05 | 1.063 | 101.4 | 1.601 | 101.5 | 424.9602 | 538.4 | 2254.1731 | 639.9 | 2679.1333
0.1 | 1.113 | 102.6 | 1.533 | 102.8 | 430.403 | 537.7 | 2251.2424 | 640.5 | 2681.6454
0.15 | 1.163 | 105.1 | 1.471 | 104.1 | 435.8459 | 536.9 | 2247.8929 | 641 | 2683.7388
0.2 | 1.213 | 106.2 | 1.414 | 105.3 | 440.87 | 536.2 | 2244.9622 | 641.5 | 2685.8322
0.3 | 1.313 | 107.4 | 1.312 | 107.6 | 450.4997 | 534.7 | 2238.682 | 642.3 | 2689.1816
0.4 | 1.413 | 109.5 | 1.225 | 109.8 | 459.7106 | 533.3 | 2232.8204 | 643.1 | 2692.5311
0.5 | 1.513 | 111.6 | 1.149 | 111.9 | 468.5029 | 531.9 | 2226.9589 | 643.8 | 2695.4618
0.6 | 1.613 | 113.5 | 1.038 | 113.8 | 476.4578 | 530.6 | 2221.5161 | 644.4 | 2697.9739
0.7 | 1.713 | 115.4 | 1.024 | 115.7 | 484.4128 | 529.5 | 2216.9106 | 645.2 | 2701.3234
0.8 | 1.813 | 117.1 | 0.971 | 117.5 | 491.949 | 528.3 | 2211.8864 | 645.8 | 2703.8354
0.9 | 1.913 | 118.8 | 0.923 | 119.2 | 499.0666 | 527.1 | 2206.8623 | 646.3 | 2705.9288
1 | 2.013 | 120.4 | 0.881 | 120.8 | 505.7654 | 526 | 2202.2568 | 646.8 | 2708.0222
1.1 | 2.113 | 121.9 | 0.841 | 122.4 | 512.4643 | 525.1 | 2198.4887 | 647.5 | 2710.953
1.2 | 2.213 | 123.4 | 0.806 | 124 | 519.1632 | 524.1 | 2194.3019 | 648.1 | 2713.4651
1.3 | 2.313 | 124.9 | 0.773 | 125.4 | 525.0247 | 523.1 | 2190.1151 | 648.5 | 2715.1398
1.4 | 2.413 | 126.3 | 0.743 | 126.8 | 530.8862 | 522.2 | 2186.347 | 649 | 2717.2332
1.5 | 2.513 | 127.6 | 0.714 | 128.1 | 536.3291 | 521.1 | 2181.7415 | 649.2 | 2718.0706
1.6 | 2.613 | 128.9 | 0.689 | 129.5 | 542.1906 | 520.4 | 2178.8107 | 649.9 | 2721.0013
1.7 | 2.713 | 130.1 | 0.665 | 130.7 | 547.2148 | 519.5 | 2175.0426 | 650.2 | 2722.2574
1.8 | 2.813 | 131.4 | 0.643 | 132 | 552.6576 | 518.6 | 2171.2745 | 650.6 | 2723.9321
1.9 | 2.913 | 132.5 | 0.622 | 133.2 | 557.6818 | 517.8 | 2167.925 | 651 | 2725.6068
2 | 3.013 | 133.7 | 0.603 | 134.4 | 562.7059 | 517 | 2164.5756 | 651.4 | 2727.2815
2.2 | 3.213 | 135.9 | 0.568 | 136.6 | 571.9169 | 515.5 | 2158.2954 | 652.1 | 2730.2123
2.4 | 3.413 | 138 | 0.536 | 138.8 | 581.1278 | 514 | 2152.0152 | 652.8 | 2733.143
2.6 | 3.613 | 140 | 0.509 | 140.8 | 589.5014 | 512.6 | 2146.1537 | 653.4 | 2735.6551
2.8 | 3.813 | 141.9 | 0.483 | 142.8 | 597.875 | 511.2 | 2140.2922 | 654 | 2738.1672
3 | 4.013 | 143.7 | 0.461 | 144.7 | 605.83 | 509.9 | 2134.8493 | 654.6 | 2740.6793
3.2 | 4.213 | 145.4 | 0.44 | 146.4 | 612.9475 | 508.6 | 2129.4065 | 655 | 2742.354
3.4 | 4.413 | 147.2 | 0.422 | 148.2 | 620.4838 | 507.4 | 2124.3823 | 655.6 | 2744.8661
3.6 | 4.613 | 148.8 | 0.405 | 149.9 | 627.6013 | 506.1 | 2118.9395 | 656 | 2746.5408
3.8 | 4.813 | 150.4 | 0.389 | 151.5 | 634.3002 | 505 | 2114.334 | 656.5 | 2748.6342
4 | 5.013 | 152 | 0.374 | 153.1 | 640.9991 | 503.8 | 2109.3098 | 656.9 | 2750.3089
4.2 | 5.213 | 153.4 | 0.361 | 154.6 | 647.2793 | 502.7 | 2104.7044 | 657.3 | 2751.9836
4.4 | 5.413 | 154.8 | 0.348 | 156.1 | 653.5595 | 501.6 | 2100.0989 | 657.7 | 2753.6584
4.6 | 5.613 | 156.2 | 0.336 | 157.6 | 659.8397 | 500.6 | 2095.9121 | 658.2 | 2755.7518
4.8 | 5.813 | 157.6 | 0.325 | 159 | 665.7012 | 499.5 | 2091.3066 | 658.5 | 2757.0078
5 | 6.013 | 158.9 | 0.315 | 160.3 | 671.144 | 498.5 | 2087.1198 | 658.8 | 2758.2638
5.5 | 6.513 | 162.1 | 0.292 | 163.6 | 684.9605 | 496.1 | 2077.0715 | 659.7 | 2762.032
6 | 7.013 | 165 | 0.272 | 166.7 | 697.9396 | 493.8 | 2067.4418 | 660.5 | 2765.3814
6.5 | 7.513 | 167.8 | 0.255 | 169.6 | 710.0813 | 491.6 | 2058.2309 | 661.2 | 2768.3122
7 | 8.013 | 170.5 | 0.24 | 172.4 | 721.8043 | 489.4 | 2049.0199 | 661.8 | 2770.8242
7.5 | 8.513 | 173 | 0.227 | 175.1 | 733.1087 | 487.4 | 2040.6463 | 662.5 | 2773.755
8 | 9.013 | 175.4 | 0.215 | 177.6 | 743.5757 | 485.4 | 2032.2727 | 663 | 2775.8484
8.5 | 9.513 | 177.7 | 0.204 | 180 | 753.624 | 483.5 | 2024.3178 | 663.5 | 2777.9418
9 | 10.013 | 180 | 0.194 | 182.3 | 763.2536 | 481.6 | 2016.3629 | 663.9 | 2779.6165
9.5 | 10.513 | 182.1 | 0.185 | 184.6 | 772.8833 | 479.8 | 2008.8266 | 664.4 | 2781.7099
10 | 11.013 | 184.1 | 0.177 | 186.8 | 782.0942 | 478 | 2001.2904 | 664.8 | 2783.3846
11 | 12.013 | 188 | 0.163 | 190.9 | 799.2601 | 474.6 | 1987.0553 | 665.5 | 2786.3154
12 | 13.013 | 191.7 | 0.151 | 194.8 | 815.5886 | 471.4 | 1973.6575 | 666.2 | 2789.2462
13 | 14.013 | 195.1 | 0.141 | 198.5 | 831.0798 | 468.3 | 1960.6784 | 666.8 | 2791.7582
14 | 15.013 | 198.3 | 0.132 | 202 | 845.7336 | 465.3 | 1948.118 | 667.3 | 2793.8516
15 | 16.013 | 201.4 | 0.124 | 205.3 | 859.55 | 462.5 | 1936.395 | 667.8 | 2795.945
16 | 17.013 | 204.4 | 0.117 | 208.5 | 872.9478 | 459.7 | 1924.672 | 668.2 | 2797.6198
17 | 18.013 | 207.2 | 0.11 | 211.5 | 885.5082 | 457 | 1913.3676 | 668.5 | 2798.8758
18 | 19.013 | 209.9 | 0.105 | 214.43 | 897.7755 | 454.4 | 1902.4819 | 668.8 | 2800.1318
19 | 20.013 | 212.5 | 0.1 | 217.2 | 909.373 | 451.8 | 1891.5962 | 669 | 2800.9692
20 | 21.013 | 215 | 0.095 | 220 | 921.096 | 449.4 | 1881.5479 | 669.4 | 2802.6439
21 | 22.013 | 217.3 | 0.09 | 222.6 | 931.9817 | 447 | 1871.4996 | 669.6 | 2803.4813
22 | 23.013 | 219.6 | 0.087 | 225.1 | 942.4487 | 444.6 | 1861.4513 | 669.7 | 2803.9
23 | 24.013 | 221.8 | 0.083 | 227.6 | 952.9157 | 442.2 | 1851.403 | 669.8 | 2804.3186
24 | 25.013 | 224 | 0.08 | 230 | 962.964 | 440 | 1842.192 | 670 | 2805.156
25 | 26.013 | 226.1 | 0.077 | 232.3 | 972.5936 | 437.7 | 1832.5624 | 670 | 2805.156
26 | 27.013 | 228.1 | 0.0741 | 234.3 | 980.9672 | 435 | 1821.258 | 669.3 | 2802.2252
27 | 28.013 | 230.1 | 0.0714 | 236.5 | 990.1782 | 432.8 | 1812.047 | 669.4 | 2802.6439
28 | 29.013 | 232 | 0.069 | 238.7 | 999.3892 | 430.7 | 1803.2548 | 669.4 | 2802.6439
29 | 30.013 | 233.9 | 0.0667 | 240.8 | 1008.1814 | 428.6 | 1794.4625 | 669.4 | 2802.6439
30 | 31.013 | 235.7 | 0.0645 | 242.9 | 1016.9737 | 426.5 | 1785.6702 | 669.4 | 2802.6439
32 | 33.013 | 239.3 | 0.0606 | 246.8 | 1033.3022 | 422.5 | 1768.923 | 669.4 | 2802.6439
34 | 35.013 | 242.6 | 0.0571 | 250.7 | 1049.6308 | 418.6 | 1752.5945 | 669.2 | 2801.8066
36 | 37.013 | 245.8 | 0.0539 | 254.3 | 1064.7032 | 414.7 | 1736.266 | 669.1 | 2801.3879
38 | 39.013 | 248.9 | 0.0511 | 257.9 | 1079.7757 | 411 | 1720.7748 | 668.9 | 2800.5505
40 | 41.013 | 251.9 | 0.0485 | 261.3 | 1094.0108 | 407.3 | 1705.2836 | 668.6 | 2799.2945

## Calculos (hidden)
Linha pressão | Gauge Pressure - Pm (bar) | Absolute Pressure - Pa (bar) | Temperature - T (°C) | Specific Volume - V (m3/Kg) | Specific Enthalpy of Liquid - he (Kcal/Kg) | Specific Enthalpy of Liquid - he (KJ/Kg) | Specific Enthalpy of Vaporization - r (Kcal/Kg) | Specific Enthalpy of Vaporization - r (KJ/Kg) | Specific Enthalpy of Saturated Steam - hg (Kcal/Kg) | Specific Enthalpy of Saturated Steam - hg (KJ/Kg)
17 | 1.4 | 2.413 | 126.3 | 0.743 | 126.8 | 530.8862 | 522.2 | 2186.347 | 649 | 2717.2332